Table E-7 : Salient Feature of ECBC-2017

2.	Scope

The code is applicable to buildings or building complexes that have a connected load of 500 kW or greater or a contract demand of 600 kVA or greater.

Generally buildings or buildings complexes having conditioned area of 1000 sq. m or more will fall under this category.

The code would become mandatory as and when it is notified by the central and state government in the official Gazette under clause (p) of Section 14 or clause (a) of section (15) of the Energy Conservation Act 2001. (52 of 2001).

2.1	Applicable Building Systems

The provisions of this code apply to:

(a)	Building envelops, except for unconditioned storage spaces or warehouses,

(b)	Mechanical systems and equipment, including heating, ventilating, and air conditioning,

(c)	Service hot water heating,

(d)	Interior and exterior lighting, and

(e)	Electrical power and motors.

2.2	Exemptions

The provisions of this code do not apply to:

(a)	Buildings that do not use either electricity or fossil fuel,

(b)	Equipment and portions of building systems that use energy primarily for manufacturing processes, and

2.3	Safety, Health and Environmental Codes Take Precedence

Where this code is found to conflict with safety, health, or environmental codes, the safety, health, or environmental codes shall take precedence.

2.4	Reference Standards

National Building Code 2005 is the reference document/ standard for lighting levels, HVAC, comfort levels, natural ventilation, pump and motor efficiencies, transformer efficiencies and any other building materials and system performance criteria.

3.	Administration and Enforcement

3.1	Compliance Requirements

3.1.1	Mandatory Requirements

Compliance with the requirements of this energy code shall be mandatory for all applicable buildings discussed in §2.

3.1.2	New Buildings

New buildings shall comply with either the provisions of §4 through §8 of this code or the Energy Budget Method of §10.

3.1.3	Additions to Existing Buildings

Where the addition plus the existing building exceeds the conditioned floor area threshold of §2, additions shall comply with the provisions of §4 through §8.  Compliance may be demonstrated in either of the following ways:

(a)	The addition alone shall comply with the applicable requirements, or

(b)	The addition, together with the entire existing building, shall comply with the requirements of this code that would apply to the entire building, as if it were a new building.

Exception to § 3.1.3: When space conditioning is provided by existing systems and equipment, the existing systems and equipment need not comply with this code.  However, any new equipment installed must comply with specific requirements applicable to that equipment.

3.1.4	Alterations to Existing Buildings

Where the existing buildings exceeds the conditioned floor area threshold in §2, portions of a building and its systems that are being altered shall meet the provisions of §4 through §8.  The specific requirements for alterations are described in the following subsections.

Exception to § 3.1.4: When the entire building complies with all of the provisions of §4 through §8 as if it were a new building.

3.1.4.1	Building Envelope

Alterations to the building envelope shall comply with the requirements of §4 for fenestration, insulation, and air leakage applicable to the portions of the buildings and its systems being altered.

Exception to §3.1.4.1:  The following alterations need not comply with these requirements provided such alterations do not increase the energy usage of the building.

(a)	Replacement of glass in an existing sash and frame, provided the U-factor and SHGC of the replacement glazing are equal to or lower than the existing glazing,

(b)	Modifications to roof/ceiling, wall, or floor cavities, which are insulated to full depth with insulation, and

(c)	Modifications to walls and floors without cavities and where no new cavities are created.

3.1.4.2	Heating, Ventilation and Air Conditioning

Alterations to building heating, ventilating, and air-conditioning equipment or systems shall comply with the requirements of §5 applicable to the portions of the building and its systems being altered.  Any new equipment or control devices installed in conjunction with the alteration shall comply with the specific requirements applicable to that equipment or control device.

3.1.4.3	Service Water Heating

Alterations to building service water heating equipment or systems shall comply with the requirements of §6 applicable to the portions of the building and its systems being altered.  Any new equipments or control devices installed in conjunction with the alteration shall comply with the specific requirements applicable to that equipment or control device.

3.1.4.4	Lighting

Alterations to building lighting equipment or systems shall comply with the requirements of § 7 applicable to the portions of the building and its systems being altered.  New lighting systems, including controls, installed in an existing building and any change of building area type as listed in Table 7.3.1 shall be considered an alteration.  Any new equipment or control devices installed in conjunction with the alteration shall comply with the specific requirements applicable to that equipment or control device.

Exception to § 3.1.4.4:  Alterations that replace less than 50% of the luminaires in a space need not comply with these requirements provided such alterations do not increase the connected lighting load.

3.1.4.5	Electric Power and Motors

Alterations to building electric power systems and motor shall comply with the requirements of § 8 applicable to the portions of the building and its systems being altered.  Any new equipment or control devices installed in conjunction with the alteration shall comply with the specific requirements applicable to that equipment or control device.

3.2	Compliance Approaches

The building shall comply with the mandatory provisions (§ 4.2, § 5.2, § 6.2, § 7.2, and § 8.2) and either of the

(a)	Prescriptive Method (§ 4.3, § 5.3, § 7.3 and § 7.4), or

Exception to § 3.2(a): The envelope trade-off option of § 4.4 may be used in place of the prescriptive criteria of § 4.3.

(b)	Energy Budget Method (Appendix 10).

3.3	Administrative Requirements

Administrative requirements relating to permit requirements, enforcement, interpretations, claims of exemption, approved calculation methods, and rights of appeal are specified by the authority having jurisdiction.

3.4	Compliance Documents

3.4.1	General

Plans and specifications shall show all pertinent data and features of the building, equipment, and systems in sufficient detail to permit the authority having jurisdiction to verify that the building complies with the requirements of this code.  Details shall include, but are not limited to:

(a)	Building Envelope: insulation materials and their R-values; fenestration U-factors, solar heat gain coefficients (SHGC), visible light transmittance (if the trade-off procedure is used), and air leakage; overhangs and sidefins, building envelope sealing details;

(b)	Heating, Ventilation, and Air Conditioning: system and equipment types, sizes, efficiencies, and controls; economizers; variable speed drives; piping insulation; duct sealing, insulation and location; requirement for balance report;

(c)	Service Hot Water and Pumping: solar water heating system

(d)	Lighting: lighting schedule showing type, number, and wattage of lamps and ballasts; automatic lighting shutoff, occupancy sensors, and other lighting controls; lamp efficacy for exterior lamps;

(e)	Electrical Power: electric schedule showing transformer losers, motor efficiencies, and power factor correction devices; electric check metering and monitoring system.

3.4.2	Supplemental Information

The authority having jurisdiction may require supplemental information necessary to verify compliance with this code, such as calculations, worksheets, compliance forms, manufacturer’s literature, or other data.

4.	Envelope

4.1	General

The building envelope shall comply with the mandatory provisions of § 4.2 and either the prescriptive criteria of § 4.3 or the trade-off option of § 4.4.

4.2	Mandatory Requirements

4.2.1		Fenestration

4.2.1.1	U-factors

U-factors shall be determined for the overall fenestration product (including the sash and frame) in accordance with ISO-15099, as specified in Appendix 11, by an accredited independent laboratory, and labeled and certified by the manufacturer or other responsible party.  U-factors for sloped glazing and skylights shall be determined at a slope of 20 degrees above the horizontal.  For unrated products, use the default table in Appendix 11.

4.2.1.2	Solar Heat Gain Coefficient (SHGC)

SHGC shall be determined for the overall fenestration product (including the sash and frame) in accordance with ISO-15099, as specified in Appendix 11, by an accredited independent laboratory, and labeled and certified by the manufacturer or other responsible party.

Exceptions to § 4.2.1.2:

(a)	Shading coefficient (SC) of the center glass alone multiplied by 0.86 is an acceptable alternate for compliance with the SHGC requirements for the overall fenestration area.

(b)	Solar heat gain coefficient (SHGC) of the glass alone is an acceptable alternate for compliance with the SHGC requirements for the overall fenestration product.

4.2.1.3	Air Leakage

Air leakage for glazed swinging entrance doors and revolving doors shall not exceed 5.0 l/s-m2.  Air leakage for other fenestration and doors shall not exceed 2.0 l/s-m2.

4.2.2	Opaque Construction

U-factors shall be determined from the default tables in Appendix 11 or determined from data or procedures contained in the ASHRAE Fundamentals, 2005.

4.2.3.    Building Envelope Sealing

The following areas of the enclosed building envelope shall be sealed, caulked, gasketed, or weather-stripped to minimize air leakage:

(a)	Joints around fenestration and door frames.

(b)	Openings between walls and foundations and between walls and roof and wall panels,

(c)	Openings at penetrations of utility services through, roots, walls, and floors

(d)	Site-built fenestration and doors,

(e)	Building assemblies used as ducts or plenums, and

(f)	All other openings in the building envelope.

4.3	Prescriptive Requirements

4.3.1	Roofs

Roofs shall comply with either the maximum assembly U-factor or the minimum insulation R-value in Table 4.3.1. R-value is for the insulation alone and does not include building materials or air films.  The roof insulation shall not be located on a suspended ceiling with removable ceiling panels.

| Table 4.3.1 Roof assembly U-factor and Insulation R-value Requirements* |
| --- |
| Climate Zone | 24-Hour use buildings Hospitals, Hotels, Call Centers etc. | Daytime use buildings Other Building Types |
|  | Maximum U-factor of the overall assembly (W/m2-0C) | Minimum R-value of insulation alone (m2-0C/W) | Maximum U-factor of the overall assembly (W/m2-0C) | Minimum R-value of insulation alone (m2-0C/W) |
| Composite | U-0.261 | R-3.5 | U-0.409 | R-2.1 |
| Hot and Dry | U-0.261 | R-3.5 | U-0.409 | R-2.1 |
| Warm and Humid | U-0.261 | R-3.5 | U-0.409 | R-2.1 |
| Moderate | U-0.409 | R-2.1 | U-0.409 | R-2.1 |
| Cold | U-0.261 | R-3.5 | U-0.409 | R-2.1 |

*See Appendix 11.3 for typical complying roof constructions.

4.3.1.1	Cool Roofs

Roofs with slopes less than 20 degrees shall have an initial solar reflectance of no less than 0.70 and an initial emittance no less than 0.75.  Solar reflectance shall be determined in accordance with ASTM E903.96 and emittance shall be determined in accordance with ASTM E408.71 (RA 1996).

4.3.2	Opaque Walls

Opaque walls shall comply with either the maximum assembly U-factor or the minimum insulation R-value in Table 4.3.2. R-value is for the insulation alone and does not include building materials or air films.

| Table 4.3.2 Opaque Wall Assembly U-factor and Insulation R-value Requirements |
| --- |
| Climate Zone | Hospitals, Hotels, Call Centers etc. (24-Hour) | Other Building Types (Daytime) |
|  | Maximum U-factor of the overall assembly (W/m2-0C) | Minimum R-value of insulation alone (m2-0C/W) | Maximum U-factor of the overall assembly (W/m2-0C) | Minimum R-value of insulation alone (m2-0C/W) |
| Composite | U-0.440 | R-2.10 | U-0.440 | R-2.10 |
| Hot and Dry | U-0.440 | R-2.10 | U-0.440 | R-2.10 |
| Warm and Humid | U-0.440 | R-2.10 | U-0.440 | R-2.10 |
| Moderate | U-0.431 | R-1.80 | U-0.397 | R-2.00 |
| Cold | U-0.369 | R-2.20 | U-0.352 | R-2.35 |

*See Appendix 11.4 for typical complying roof constructions.

4.3.3	Vertical Fenestration

Vertical fenestration shall comply with the maximum area weighted U-factor and maximum area weighted SHGC requirements of Table 4.3.3-1.  Vertical fenestration area is limited to a maximum of 60% of the gross wall area for the prescriptive requirement.

| Table 4.3.3-1 Vertical Fenestration U-factor and SHGC Requirements (U-factor in W/m2-0C) |
| --- |
|  |  | WWR=40% | 40% <WWR<=60% |
| Climate Zone | Maximum U-factor | Maximum SHGC | Maximum SHGC |
| Composite | 3.30 | 0.25 | 0.20 |
| Hot and Dry | 3.30 | 0.25 | 0.20 |
| Warm and Humid | 3.30 | 0.25 | 0.20 |
| Moderate | 6.970 | 0.40 | 0.30 |
| Cold | 3.30 | 0.51 | 0.51 |

*See Appendix 11.2.1 for typical complying vertical fenestration constructions.

Exception to § 4.3.3:  Overhangs and/or side fins may be applied in determining the SHGC for the proposed design.  An adjusted SHGC, accounting for overhangs and/or sidefins, is calculated by multiplying the SHGC of the unshaded fenestration product times a multiplication (M) factor.  If this exception is applied, a separate M Factor shall be determined for each orientation and unique shading condition by equation 13.1.2 and the overhand and side fine coefficients are available in Table 13.6 (Appendix E).

| Table 4.3.3-2 SHGC “M” Factor Adjustments for Overhangs and Fins |
| --- |
|  | Overhang “M” Factors for 4 Projection Factors | Vertical Fin “M” Factors for 4 Projection Factors | Overhang+Fin “M” Factors for 4 Projection Factors |
| Project Location | Orientation | 0.25-0.49 | -0.50- -0.74 | 0.75-0.99 | 1.00 + | 0.25- 0.49 | 0.50- 0.74 | 0.75- 0.99 | 1.00 + | 0.25- 0.49 | 0.50- 0.74 | 0.75- 0.99 | 1.00 + |
| North latitude 150 or greater | N | .88 | .80 | .76 | .73 | .74 | .67 | .58 | .52 | .64 | .51 | .39 | .31 |
|  | E/W | .79 | .65 | .56 | .50 | .80 | .72 | .65 | .60 | .60 | .39 | .24 | .16 |
|  | S | .79 | .64 | .52 | .43 | .79 | .69 | .60 | .56 | .60 | .33 | .10 | .02 |
| Less than 150 North latitude | N | .83 | .74 | .69 | .66 | .73 | .65 | .57 | .50 | .59 | .44 | .32 | .23 |
|  | E/W | .80 | .67 | .59 | .53 | .80 | .72 | .63 | .58 | .61 | .41 | .26 | .16 |
|  | S | .78 | .62 | .55 | .50 | .74 | .65 | .57 | .50 | .53 | .30 | .12 | .04 |

Exception to SHGC Requirements in § 4.3.3: Vertical Fenestration areas located more than 2.2 m (7 ft) above the level of the floor are exempt from the SHGC requirement in Table 4.3.3-1, if the following conditions are complied with:

(a)	Total Effective Aperture: The total Effective Aperture for the elevation is less than 0.25, including all fenestration areas greater than 1.0 m (3 ft) above the floor level; and,

(b)	An interior light shelf is provided at the bottom of this fenestration area, with an interior projection factor not less than:

- 1.0 for E-W, SE, SW, NE, and NW orientations

- 0.5 for S orientation, and

- 0.35 for N orientation when latitude is < 23 degrees.

4.3.3.1	Minimum Visible Transmission (VLT) of Glazing for vertical Fenestration

Vertical fenestration product shall have the minimum Visual Light Transmittance (VLT), defined as function of Window Wall Ratio (WWR), where Effective Aperture > 0.1, equal to or greater than the Minimum VT requirements of Table 4.3.3.1

| Table 4.3.3.1 Minimum VLT Requirements |
| --- |
|  | Window Wall Ratio |  | Minimum VLT |
|  | 0 . 0.3 |  | 0.27 |
|  | 0.31-0.4 |  | 0.20 |
|  | 0.41-0.5 |  | 0.16 |
|  | 0.51-0.6 |  | 0.13 |
|  | 0.61-0.7 |  | 0.11 |

4.3.4	Skylights

Skylights shall comply with the maximum U-factor and maximum SHGC requirements of Table 4.3.4 Skylight area is limited to a minimum of 5% of the gross roof area for the prescriptive requirement.

| Table 4.3.4 Skylight U-factor and SHGC Requirements (U-factor in W/m2-0C) |
| --- |
| Climate | Maximum U-factor With Curb w/o Curb | Maximum SHGC 0-2% SRR 2.1-5% SRR |
| Composite | 0 . 0.3 | 7.71 | 0.40 | 0.25 |
| Hot and Dry | 0.31-0.4 | 7.71 | 0.40 | 0.25 |
| Warm Humid | 0.41-0.5 | 7.71 | 0.40 | 0.25 |
| Moderate | 0.51-0.6 | 7.71 | 0.61 | 0.4 |
| Cold | 0.61-0.7 | 7.71 | 0.61 | 0.4 |

SRR = Skylight roof ratio which is the ratio of the total skylight are of the roof, measured to the outside of the frame, to the gross exterior roof.

See § 11.2.2 for typical complying skylight constructions.

4.4	Building Envelope Trade-off Option

The building envelope complies with the code if the building envelope performance factor (EPF) of the proposed design is less than the standard design, where the standard design exactly complies with the criteria in § 4.3.  The envelope trade-off equation is found in Appendix 12.

5.	Heating, Ventilation and Air Conditioning

5.1	General

All heating, ventilation and air conditioning equipment and systems shall comply with the mandatory provisions of § 5.2 and the prescriptive criteria of § 5.3.

5.2	Mandatory Requirements

5.2.1		Natural Ventilation

Natural ventilation shall comply with the design guidelines provided for natural ventilation in the National Building Code of India 2005 Part 8, 5.4.3 and 5.7.1.1

5.2.2		Minimum Equipment Efficiencies

Cooling equipment shall meet or exceed the minimum efficiency requirements presented in Tables 5.2.2-1 through 5.2.2-5.  Heating and cooling equipment not listed here shall comply with ASHRAE 90.1-2004 § 6.4.1.

Unitary Air Conditioner shall meet IS 1391 (Part 1), Split air conditioner shall meet IS 1391 (Part 2), Packaged air conditioner shall meet IS 8148 and Boilers shall meet IS 13980 with above 75% thermal efficiency.

| Table 5.2.2-2 Chillers |
| --- |
| Equipment Class | Minimum COP | Minimum IPLV | Test Standard |
| Air Cooled Chiller <530 kW (<150 tons) | 2.90 | 3.16 | ARI 550/590- 1998 |
| Air Cooled Chiller >=530 kW (>=150 tons) | 3.05 | 3.32 | ARI 550/590- 1998 |
| Centrifugal Water Cooled Chiller <530 kW (<150 tons) | 5.80 | 6.09 | ARI 550/590- 1998 |
| Centrifugal Water Cooled Chiller >=530 and <1050 kW (>=150 and <300 tons) | 5.80 | 6.17 | ARI 550/590- 1998 |
| Centrifugal Water Cooled Chiller >=1050 kW (>=300 tons) | 6.30 | 6.61 | ARI 550/590- 1998 |
| Reciprocating Compressor, Water Cooled Chiller all sizes | 4.20 | 5.05 | ARI 550/590- 1998 |
| Rotary Screw and Scroll Compressor, Water Cooled Chiller <530 kW (<150 tons) | 4.70 | 5.49 | ARI 550/590- 1998 |
| Rotary Screw and Scroll Compressor, Water Cooled Chiller >=530 and <1050 kW (>=150 and <300 tons) | 5.40 | 6.17 | ARI 550/590- 1998 |
| Rotary Screw and Scroll Compressor, Water Cooled Chiller >=1050 kW (>=300 tons) | 5.75 | 6.43 | ARI 550/590- 1998 |

5.2.3	Controls

5.2.3.1	All mechanical cooling and heating systems shall be controlled by a timeclock that:

(a)	Can start and stop the system under different schedules for three different day types per week,

(b)	Is capable of retaining programming and time setting during loss of power for a period of at least 10 hours, and

(c)	Includes an accessible manual override that allows temporary operation of the system for up to 2 hours.

Exceptions to 5.2.3.1:

(a)	Cooling systems < 28 kW (8 tons)

(b)	Heating system < 7 kW (2 tons)

5.2.3.2		All heating and cooling equipment shall be temperature controlled.  Where a unit provides both heating and cooling, controls shall be capable of providing a temperature dead band of 30C (50F) within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum.  Where separate heating and cooling equipment serve the same temperature zone, thermostats shall be interlocked to prevent simultaneous heating and cooling.

5.2.3.3		All cooling towers and closed circuit fluid coolers shall have either two speed motors, pony motors, or variable speed drives controlling the fans.

5.2.4.	Piping and Ductwork

5.2.4.1	Piping for heating systems with a design operating temperature of 600C (1400F) or greater shall have at least R-0.70 (R-4) insulation.  Piping for heating systems with a design operating temperature less than 600C (1400F) but greater than 400C (1400F), piping for cooling systems with a design operating temperature less than 150C (590F), and refrigerant suction piping on split systems shall have at least R-0.35 (R-2) insulation.  Insulation exposed to weather shall be protected by aluminum sheet metal, painted canvas, or plastic cover.  Cellular foam insulation shall be protected as above, be painted with water retardant paint.

Ductwork shall be insulated in accordance with Table 5.2.4.2

| Table 5.2.4.2 Ductwork Insulation (m2-0C/W) |
| --- |
| Required Insulationa |
| Duct Location | Supply Ducts |  | Return Ducts |
| Exterior | R-1.4 |  | R- 0.6 |
| Ventilated Attic | R-1.4 |  | R- 0.6 |
| Unventilated Attic Without Roof Insulation | R-1.4 |  | R- 0.6 |
| Unventilated Attic with Roof Insulation | R- 0.6 |  | No Requirement |
| Unconditioned Spaceb | R- 0.6 |  | No Requirement |
| Indirectly Conditioned Spacec | No Requirement |  | No Requirement |
| Buried | R- 0.6 |  | No Requirement |

a Insulation R-value is measured on a horizontal plane in accordance with ASTM C518 at a mean temperature of 240C (75F) at the installed thickness.

b Includes crawlspaces, both ventilated and non-ventilated

c Includes return air plenums with or without exposed roofs above.

5.2.5   System Balancing

5.2.5.1	General

Construction documents shall require that all HVAC systems be balanced in accordance with generally accepted engineering standards.

Construction documents shall require that a written balance report be provided to the owner or the designated representative of the building owner for HVAC systems serving zones with a total conditioned area exceeding 500 m2 (5,000 ft2).

5.2.5.1.1	Air System Balancing

Air systems shall be balanced in a manner to first minimize throttling losses.  Then, for fans with fan system power greater than 0.75 kW (1.0 hp), fan speed shall be adjusted to meet design flow conditions.

5.2.5.1.2	Hydronic System Balancing

Hydronic systems shall be proportionately balanced in a manner to first minimize throttling losses; then the pump impeller shall be trimmed or pump speed shall be adjusted to meet design flow conditions.

Exceptions to § 5.2.5.1.2:

(a)	Impellers need not be trimmed nor pump speed adjusted for pumps with pump

motors of 7.5 kW (10 hp) or less,

(b)	Impellers need not be trimmed when throttling results in no greater than 5% of the nameplate horsepower draw, or 2.2 kW (3 hp), whichever is greater.

5.2.6	Condensers

5.2.6.1	Condenser Locations

Care shall be exercised in locating the condensers in such a manner that heat sink is free of interference from heat discharge by devices located in adjoining spaces and also does not interfere with such other systems installed nearby.

5.2.6.2	Treated Water for Condensers

All high-rise buildings using centralized cooling water system shall use soft water for the condenser and chilled water system.

5.3	Prescriptive Requirements

Compliance shall be demonstrated with the requirements in § 5.3.1 through § 5.3.2 for each HVAC system that meets the following criteria:

(a)	Serves a single zone,

(b)	Cooling (if any) is provided by a unitary packaged or split-system air conditioner or heat pump,

(c)	Heating (if any) is provided by a unitary packaged or split-system heat pump, fuel-fired furnace, electric resistance heater, or baseboards connected to a boiler, and

(d)	Outside air quantity is less than 1,400 l/s (3000 cfm) and less than 70% of supply air at design conditions.

Other HVAC systems shall comply with ASHRAE 90.1-2004, § 6.5.

5.3.1	Economizers

5.3.1.1	Air Side Economizer

Each individual cooling fan system that has a design supply capacity over 1,200 l/s (2,500 cfm) and a total mechanical cooling capacity over 22 kW (6.3 tons) shall include either:

(a)	An air economizer capable of modulating outside-air and return-air dampers to supply 100 percent of the design supply air quantity as outside-air; or

(b)	A water economizer capable of providing 100% of the expected system cooling load at outside air temperatures of 100C (500F) dry-bulb/7.20C (450F) wet-bulb and below.

Exception to § 5.3.1.1:

(a)	Projects in the Hot-Dry and Warm-Humid climate zones are exempt.

(b)	Individual ceiling mounted fan systems < 3,200 l/s (6,500 cfm) are exempt.

5.3.1.2	Where required by 5.3.1.1 economizers shall be capable of providing partial cooling even when additional mechanical cooling is required to meet the cooling load.

5.3.1.3	Air-side economizers shall be tested in the field following the requirements in Appendix 14 to ensure proper operation.

Exception to 5.3.1.3:  Air economizers installed by the HVAC system equipment manufacturer and certified to the building department as being factory calibrated and tested per the procedures in Appendix 14.

5.3.2	Variable Flow Hydronic Systems

5.3.2.1	Chilled or hot-water systems shall be designed for variable fluid flow and shall be capable of reducing pump flow rates to no more than the larger of:

(a)	50% of the design flow rate, or

(b)	the minimum flow required by the equipment manufacturer for proper operation of the chillers or boilers.

5.3.2.2	Water cooled air-conditioning or heat pump units with a circulation pump motor greater than or equal to 3.7 kW (5 hp) shall have two-way automatic isolation valves on each water cooled air-conditioning or heat pump unit that are interlocked with the compressor to shut off condenser water flow when the compressor is not operating.

5.3.2.3	Chilled water or condenser water systems that must comply with either 5.3.2.1 or 5.3.2.2 and that have pump motors greater than or equal to 3.7 kW (5 hp) shall be controlled by variable speed drives.

6.	Service Hot Water and Pumping

6.1	General

All service water heating equipment and systems shall comply with the mandatory provisions of § 6.2.

6.2	Mandatory Requirements

6.2.1	Solar Water Heating

Residential facilities, hotels and hospitals with a centralized system shall have solar water heating for at least 1/5 of the design capacity.

Exception to § 6.2.1:  Systems that use heat recovery for at least 1/5 of the design capacity.

6.2.2	Equipment Efficiency

Service water heating equipment shall meet or exceed the performance and minimum efficiency requirements presented in available Indian Standards.

(a)		Solar water heater shall meet the performance/minimum efficiency level mentioned in IS 13129 Part (1&2)

(b)		Gas Instantaneous Water heaters shall meet the performance/minimum efficiency level mentioned in IS 15558 with above 80% thermal efficiency.

(c)		Electric water heater shall meet the performance/minimum efficiency level mentioned in IS 2082.

6.2.3	Supplementary Water Heating System

Supplementary heating system shall be designed to maximize the energy efficiency of the system and shall incorporate the following design features in cascade:

(d)		Maximum heat recovery from hot discharge system like condensers of air conditioning units,

(e)		Use of gas fired heaters wherever gas is available, and

(f)		Electric heater as last resort.

6.2.4	Piping Insulation

Piping insulation shall comply with § 5.2.4.1.  The entire hot water system including the storage tanks, pipelines shall be insulated conforming to the relevant IS standards on materials and applications.

6.2.5	Heat Traps

Vertical pipe risers serving storage water heaters and storage tanks not having integral heat traps and serving a non-recirculating system shall have heat traps on both the inlet and outlet piping as close as practical to the storage tank.

6.2.6	Swimming Pools

Heated pools shall be provided with a vapor retardant pool cover on or at the water surface.  Pools heated to more than 320C (900F) shall have a pool cover with a minimum insulation value of R-2.1 (R-12).

Exception to § 6.2.6: Pools deriving over 60% of their energy from site-recovered energy or solar energy source.

6.2.7	Compliance Documentation

The application for approval shall furnish detailed calculation showing the design to ensure that at least 20% of the heating requirement shall be met from solar heat/heat recovery and not more than 80% of the heat shall be met from electrical heating.  Wherever gas is available, not more than 20% of the heat shall be met from electrical heating.

7.	Lighting

7.1	  General

Lighting systems and equipment shall comply with the mandatory provisions of § 7.2 and the prescriptive criteria of § 7.3 and § 7.4.  The lighting requirements in this section shall apply to:

(a)		Interior spaces of buildings,

(b)		Exterior building features, including facades, illuminated roofs, architectural features, entrances, exits, loading docks, and illuminated canopies, and,

(c)		Exterior building grounds lighting that is provided through the building’s electrical service.

Exceptions to § 7.1:

(a)		Emergency lighting that is automatically off during normal building operation and is powered by battery, generator, or other alternate power source; and,

(b)		Lighting in dwelling units.

7.2	  Mandatory Requirements

7.2.1		Lighting Control

7.2.1.1		 Automatic Lighting Shutoff

Interior lighting systems in buildings larger than 500 m2 (5,000 ft2) shall be equipped with an automatic control device.  Within these buildings, all office areas less than 30 m2 (300 ft2) enclosed by walls or ceiling-height partitions, all meeting and conference rooms, all school classrooms, and all storage spaces shall be equipped with occupancy sensors.  For other spaces, this automatic control device shall function on either:

(a)		A scheduled basis at specific programmed times.  An independent program schedule shall be provided for areas of no more than 2,500 m2 (25,000 ft2) and not more than one floor; or,

(b)		Occupancy sensors that shall turn the lighting off within 30 minutes of an occupant leaving the space.  Light fixtures controlled by occupancy sensors shall have a wall-mounted, manual switch capable of turning off lights when the space is occupied.

Exception to § 7.2.1.1:  Lighting systems designed for 24-hour use.

7.2.1.2	   Space Control

Each space enclosed by ceiling-height partitions shall have at least one control device to independently control the general lighting within the space.  Each control device shall be activated either manually by an occupant or automatically by sensing an occupant.  Each control device shall:

(a)		Control a maximum of 250 m2 (2,500 ft2) for a space less than or equal to 1,000 m2 (10,000 ft2), and a maximum of 1,000 m2 (10,000 ft2) for a space greater than 1,000 m2 (10,000 ft2).

(b)		Be capable of overriding the shutoff control required in 7.2.1.1 for no more than  2 hours, and

(c)		Be readily accessible and located so the occupant can see the control.

Exception to § 7.2.1.2(c):  The required control device may be remotely installed if required for reasons of safety or security.  A remotely located device shall have a pilot light indicator as part of or next to the control device and shall be clearly labeled to indentify the controlled lighting.

7.2.1.3		Control in Daylighted Areas

Luminaires in daylighted areas greater than 25 m2 (250 ft2) shall be equipped with either a manual or automatic control device that:

(a)		Is capable of reducing the light output of the luminaires in the daylighted areas by at least 50%, and

(b)		Controls only the luminaires located entirely within the daylighted area.

7.2.1.4		Exterior Lighting Control

Lighting for all exterior applications not exempted in § 7.4 shall be controlled by a photosensor or astronomical time switch that is capable of automatically turning off the exterior lighting when daylight is available or the lighting is not required.

7.2.1.5		Additional Control

The following lighting applications shall be equipped with a control device to control such lighting independently of general lighting:

(a)		Display/Accent Lighting:  Display or accent lighting greater than 300 m2       (3,000 ft2) area shall have a separate control device.

(b)		Case Lighting:  Lighting in cases used for display purposes greater than 300 m2 (3000 ft2) area shall be equipped with a separate control device.

(c)		Hotel and Motel Guest Room Lighting:  Hotel and motel guest rooms and guest suites shall have a master control device at the main room entry that controls all permanently installed luminaires and switched receptacles.

(d)		Task Lighting:  Supplemental task lighting including permanently installed under shelf or under cabinet lighting shall have a control device integral to the luminaires or be controlled by a wall-mounted control device provided the control device complies with 7.2.1.2 (c).

(e)		Nonvisual Lighting:  Lighting for nonvisual applications, such as plant growth and food-warming, shall be equipped with a separate control device.

(f)		Demonstration Lighting:  Lighting equipment that is for sale or for demonstrations in lighting education shall be equipped with a separate control device accessible only to authorized personnel.

7.2.2		Exit Signs

Internally-illuminated exit signs shall not exceed 5 W per face.

7.2.3		Exterior Building Grounds Lighting

Lighting for exterior building grounds luminaires which operate at greater than 100 W shall contain lamps having a minimum efficacy of 60 lm/W unless the luminaire is controlled by a motion sensor or exempt under § 7.1.

7.3		Interior Lighting Power

The installed interior lighting power for a building or a separately metered or permitted portion of a building shall be calculated in accordance with § 7.3.3 and shall not exceed the interior lighting power allowance determined in accordance with either § 7.3.1 or § 7.3.2.  Tradeoffs of interior lighting power allowance among portions of the building for which a different method of calculation has been used are not permitted.

Exception to § 7.3:  The following lighting equipment and applications shall not be considered when determining the interior lighting power allowance, nor shall the wattage for such lighting be included in the installed interior lighting power.  However, any such lighting shall not be exempt unless it is an addition to general lighting and is controlled by an independent control device.

(a)		Display or accent lighting that is an essential element for the function performed in galleries, museums, and monuments,

(b)		Lighting that is integral to equipment or instrumentation and is installed by its manufacturer,

(c)		Lighting specifically designed for medical or dental procedures and lighting integral to medical equipment.

(d)		Lighting integral to food warming and food preparation equipment,

(e)		Lighting for plant growth or maintenance,

(f)		Lighting in spaces specifically designed for use by the visually impaired,

(g)		Lighting in retail display windows, provided the display area is enclosed by ceiling-height partitions,

(h)		Lighting in interior spaces that have been specifically designate as a registered interior historic landmark.

(i)		Lighting that is an integral part of advertising or directional signage,

(j)		Exist signs,

(k)		Lighting that is for sale or lighting educational demonstration systems,

(l)		Lighting for theatrical purposes, including performance, stage, and film or video production, and

(m)		Athletic playing areas with permanent facilities for television broadcasting.

7.3.1		Building Area Method

Determination of interior lighting power allowance (watts) by the building area method shall be in accordance with the following:

(a)		Determine the allowed lighting power density from Table 7.3.1 for each appropriate building area type.

(b)		Calculate the gross lighted floor are for each building area type.

(c)		The interior lighting power allowance is the sum of the products of the gross lighted floor area of each building are times the allowed lighting power density for that building area types.

| Table 7.3.1 Interior Lighting Power – Building Area Method |
| --- |
| Building Area Type | LPD (W/m2) | Building Area Type | LPD (W/m2) |
| Automotive Facility | 9.7 | Multifamily Residential | 7.5 |
| Convention Center | 12.9 | Museum | 11.8 |
| Dining: Bar Lounge/Leisure | 14.0 | Office | 10.8 |
| Dining: Cafeteria/Fast Food | 15.1 | Parking Garage | 3.2 |
| Dining: Family | 17.2 | Performing Arts Theater | 17.2 |
| Dormitory/Hostel | 10.8 | Police/Fire Station | 10.8 |
| Gymnasium | 11.8 | Post Office/Town Hall | 11.8 |
| Healthcare-Clinic | 10.8 | Religious Building | 14.0 |
| Hospital/Health Care | 12.9 | Retail/Mail | 16.1 |
| Hotel | 10.8 | School/University | 12.9 |
| Library | 14.0 | Sports Arena | 11.8 |
| Manufacturing Facility | 14.0 | Transportation | 10.8 |
| Motel | 10.8 | Warehouse | 8.6 |
| Motion Picture Theater | 12.9 | Workshop | 15.1 |

In cases where both a general building are type and a specific building are type are listed, the specific building area type shall apply.

7.3.2		Space Function Method

Determination of interior lighting power allowance (watts) by the space function method shall be in accordance with the following:

(a)		Determine the appropriate building type from Table 7.3.2 and the allowed lighting power density.

(b)		For each space enclosed by partitions 80% or greater than ceiling height, determine the gross interior floor area by measuring to the center of the partition wall.  Include the floor are of balconies or other projections.  Retail spaces do not have to comply with the 80% partition height requirements.

(c)		The interior lighting power allowance is the sum of the lighting power allowance for all spaces.  The lighting power allowance for a space is the product of the gross lighted floor area of the space times the allowed lighting power density for that space.

| Table 7.3.2 Interior Lighting Power – Space Function Method |
| --- |
| Space Function | LPD (W/m2) | Space Function | LPD (W/m2) |
| Office-enclosed | 11.8 | Library |  |
| Office-open Plan | 11.8 | Card File & Cataloging | 11.8 |
| Conference/Meeting/Multipurpose | 14.0 | Stacks | 18.3 |
| Classroom/Lecture/Training | 15.1 | Reading Area | 12.9 |
| Lobby | 14.0 | Hospital |  |
| For Hotel | 11.8 | Emergency | 29.1 |
| For Performing Arts Theater | 35.5 | Recovery | 8.6 |
| For Motion Picture Theater | 11.8 | Nurse Station | 10.8 |
| Audience/Seating Area | 9.7 | Exam Treatment | 16.1 |
| For Gymnasium | 4.3 | Pharmacy | 12.9 |
|  |  | Patient Room | 7.5 |
| For Convention Center | 7.5 | Operating Room | 23.7 |
| For Religious Buildings | 18.3 | Nursery | 6.5 |
| For Sports Arena | 4.3 | Medical Supply | 15.1 |
| For Performing Arts Theater | 28.0 | Physical Therapy | 9.7 |
| For Motion Picture Theater | 12.9 | Radiology | 4.3 |
| For Transportation | 5.4 | Laundry – Washing | 6.5 |
| Atrium-first three floors | 6.5 | Automotive- Service Repair | 7.5 |
| Atrium-each additional floor | 2.2 | Manufacturing |  |
| Lounge/Recreation | 12.9 | Low Bay (<8m ceiling) | 12.9 |
| For Hospital | 8.6 | High Bay (>8m ceiling) | 18.3 |
| Dining Area | 9.7 | Detailed Manufacturing | 22.6 |
| For Hotel | 14.0 | Equipment Room | 12.9 |
| For Motel | 12.9 | Control Room | 5.4 |
| For Bar Lounge/Leisure Dining | 15.1 | Hotel/Motel Guest Rooms | 11.8 |
| For Family Dining | 22.6 | Dormitory – Living Quarters | 11.8 |
| Food Preparation | 12.9 | Museum |  |
| Laboratory | 15.1 | General Exhibition | 10.8 |
| Restrooms | 9.7 | Restoration | 18.3 |
| Dressing/Locker/Fitting Room | 6.5 | Bank Office – Banking Activity Area | 16.1 |
| Corridor/Transition | 5.4 | Retail |  |
| For Hospital | 10.8 | Sales Area | 18.3 |
| For Manufacturing Facility | 5.4 | Mall Concourse | 18.3 |
| Stairs-active | 6.5 | Sports Arena |  |
| Active Storage | 8.6 | Ring Sports Area | 29.1 |
| For Hospital | 9.7 | Court Sports Area | 24.8 |
| Inactive Storage | 3.2 | Indoor Field Area | 15.1 |
| For Museum | 8.6 | Warehouse |  |
| Electrical/Mechanical | 16.1 | Fine Material Storage | 15.1 |
| Workshop | 20.5 | Medium/Bulky Material Storage | 9.7 |
| Sleeping Quarters | 3.2 | Parking Garage – Garage Area | 2.2 |
| Convention Center – Exhibit Space | 14.0 | Transportation |  |
|  |  | Airport – Concourse | 6.5 |
|  |  | Air/Train/Bus – Baggage Area | 10.8 |
|  |  | Ticket Counter | 16.1 |

7.3.3		Installed Interior Lighting Power

The installed interior lighting power calculated for compliance with § 7.3 shall include all power used by the luminaires, including lamps, ballasts, current regulators, and control devices except as specifically exempted in § 7.1.

Exception to § 7.3.3: If two or more independently operating lighting systems in a space are controlled to prevent simultaneous user operation, the installed interior lighting power shall be based solely on the lighting system with the highest power.

7.3.3.1		Luminaire Wattage

Luminaire wattage incorporated into the installed interior lighting power shall be determined in accordance with the following:

(a)		The wattage of incandescent luminaires with the medium base sockets and not containing permanently installed ballasts shall be the maximum labeled wattage of the luminaires.

(b)		The wattage of luminaires containing permanently installed ballasts shall be the operating input wattage of the specified lamp/ballast combination based on values from manufacturers’ catalogs or values from independent testing laboratory reports.

(c)		The wattage of all other miscellaneous luminaire types not described in (a) or (b) shall be the specified wattage of the luminaires.

(d)		The wattage of lighting track, plug-in busway, and flexible-lighting systems that allow the addition and/or relocation of luminaires without altering the wiring of the system shall be the larger of the specified wattage of the luminaires included in the system or 135 W/m (45 W/ft).  Systems with integral overload protection, such as fuses or circuit breakers, shall be rated at 100% of the maximum rated load of the limiting device.

7.4		Exterior Lighting Power

For building exterior lighting applications specified in Table 7.4, the connected lighting power shall not exceed the specified lighting limits specified for each of these applications.  Trade-offs between applications are not permitted.  Exterior lighting for all other applications (except those included in the Exceptions to § 7.4) shall comply with the requirements of § 7.2.3.

| Table 7.4 Exterior Building Lighting Power |
| --- |
| Exterior Lighting Applications |  | Power Limits |  |
| Building entrance (with canopy) |  | 13 W/m2 (1.3 W/ft2) of canopied area |  |
| Building entrance (without canopy) |  | 90 W/lin m (30/lin f) of door width |  |
| Building exit |  | 60 W/lin m (20 W/lin f) of door width |  |
| Building facades |  | 2 W/m2 (0.2 W/ft2) of vertical façade area |  |

Exceptions to § 7.4: Lighting used for the following exterior applications is exempt when equipped with an independent control device:

(a)		Specialized signal, directional, and marker lighting associated with transportation;

(b)		Lighting used to highlight features of public monuments and registered historic landmark structures or buildings;

(c)		Lighting that is integral to advertising signage; or

(d)		Lighting that is specifically designated as required by a health or life safety statute, ordinance, or regulation.

8.	Electrical Power

8.1		General

Electric equipment and systems shall comply with the mandatory requirements of         § 8.2.

8.2		Mandatory Requirements

8.2.1		Transformers

8.2.1.1		 Maximum Allowable Power Transformer Losses

Power transformers of the proper ratings and design must be selected to satisfy the minimum acceptable efficiency at 505 and full load rating.  In addition, the transformer must be selected such that it minimizes the total of its initial cost in addition to the present value of the cost of its total lost energy while serving its estimated loads during its respective life span.

| Table 8.2.1.1 Maximum allowable losses for Dry type distribution transformers with highest voltage for equipment 24 kV, at 50% and 100% of the load. |
| --- |
| Transformer Capacity kVA | Maximum Allowable Losses at 50% kVA or Load | Maximum Allowable Losses at full load/Rated kVA |  |
| 100 | 1.88% | 2.44% |  |
| 160 | 1.61% | 2.07% |  |
| 200 | 1.50% | 1.90% |  |
| 250 | 1.36% | 1.73% |  |
| 400 | 1.19% | 1.51% |  |
| 500 | 1.12% | 1.45% |  |
| 630 | 1.06% | 1.40% |  |
| 1000 | 0.90% | 1.20% |  |
| 1600 | 0.79% | 1.05% |  |
| 2000 | 0.75% | 1.00% |  |

Table 8.2.1.2  Maximum allowable losses for oil filled distribution transformers with highest voltage for equipment 36 kV, at 50% and 100% of the load.

| Transformer Capacity kVA |  | Maximum Allowable Losses at 50% kVA or Load |  | Maximum Allowable Losses at full load/Rated kVA |  |
| --- | --- | --- | --- | --- | --- |
| 100 |  | 1.04% |  | 1.8% |  |
| 160 |  | 0.96% |  | 1.38% |  |
| 200 |  | 0.93% |  | 1.35% |  |
| 250 |  | 0.89% |  | 1.27% |  |
| 400 |  | 0.79% |  | 1.12% |  |
| 500 |  | 0.75% |  | 1.05% |  |
| 630 |  | 0.70% |  | 0.99% |  |
| 1000 |  | 0.70% |  | 0.98% |  |
| 1600 |  | 0.65% |  | 0.98% |  |
| 2000 |  | 0.64% |  | 0.98% |  |

8.2.1.2		 Measurement and Reporting of Transformer Losses

All measurement of losses shall be carried out by using calibrated digital meters of class 0.5 or better accuracy and certified by the manufacture.  All transformers of capacity of 500 kVA and above would be equipped with additional metering class current transformers (CTs) and potential transformers (PTs) additional to requirements of Utilities so that periodic loss monitoring study may be carried out.

8.2.2		Energy Efficient Motors

Motors shall comply with the following:

(a)	All permanently wired polyphase motors of 0.375 kW or more serving the building and expected to operate more than 1,500 hours per year and all permanently wired polyphase motors of 50 kW or more serving the building and expected to operate more than 500 hours per year shall have a minimum acceptable nominal full load motor efficiency not less than IS 12615 for energy efficient motors.

(b)		Motors of horsepower differing from those listed in the table shall have efficiency greater than that of the next listed kW motor.

(c)		Motor horsepower ratings shall not exceed 200% of the calculate maximum load being served.

(d)		Motor nameplates shall list the nominal full-load motor efficiencies and the full load power factor.

(e)		Motor users should insist on proper rewinding practices for any rewound motors.  If the proper rewinding practices cannot be assured, the damaged motor should be replaced with a new, efficient one rather than suffer the significant efficiency penalty associated with typical rewind practices.

(f)		Certificates shall be obtained and kept on record indicating the motor efficiency.  Whenever a motor is rewound, appropriate measures shall be taken so that the core characteristics of the motor is not lost due to thermal and mechanical stress during removal of damaged parts.  After rewinding, a new efficiency test shall be performed and a similar record shall be maintained.

8.2.3		Power Factor Correction

All electricity supplies exceeding 100 A, 3 phase shall maintain their power factor between 0.95 lag and unity at the point of connection.

8.2.4		Check-Metering and Monitoring

(a)		Services exceeding 1000 kVA shall have permanently installed electrical metering to record demand (kVA), energy (kWh), and total power factor.  The metering shall also display current (in each phase and the neutral), voltage (between phases and between each phase and neutral), and total harmonic distortion (THD) as a percentage of total current.

(b)		Services not exceeding 1000 kVA but over 65 kVA shall have permanently installed electric metering to record demand (kW), energy (kWh), and total power factor (or kVARh).

(c)		Services not exceeding 65 kVA shall have permanently installed electrical metering to record energy (kWh).

8.2.5		Power Distribution Systems

8.2.5.1	Power Distribution System Losses

The power cabling shall be adequately sized as to maintain the distribution losses not to exceed 1% of the total power usage.  Record of design calculation for the losses shall be maintained.